{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":58,"n_cols":11,"rows_kept":58,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RZQG-L7V1/LY1"]
[]
[]
[]
[]
["","","","","","RZQG71L7V1B","RZQG71L7Y1B9","RZQG100L7Y1B","RZQG100L7V1B","RZQG125L7V1B","RZQG125L7Y1B"]
["Sound pressure level","Heating","","Nom.","dBA","50","50","52","","53","53"]
["","Cooling","","Nom.","dBA","48","48","50","","51","51"]
["Standard Accessories","أغلفة برباط","","","","2","2","2","","2","2"]
["","Installation manual","","","","1","1","1","1","1","1"]
["Refrigerant","Charge","","","TCO2Eq","6.1","6.1","8.4","","8.4","8.4"]
["","GWP","","","","2,087.5","2,087.5","2,087.5","","2,087.5","2,087.5"]
["","Charge","","","kg","2.9","2.9","4.0","","4.0","4.0"]
["","النوع","","","","R-410A","R-410A","R-410A","","R-410A","R-410A"]
["Piping connections","Liquid","","القطر الخارجي","mm","9.52","9.52","9.52","","9.52","9.52"]
["","طول الأنابيب","الحد الأعلى","الوحدة الخارجية - الوحدة الداخلية","م","50","50","75","","75","75"]
["","","نظام","بدون شحن","م","30","30","30","","30","30"]
["","","","مكافئ","م","70","70","90","","90","90"]
["","غاز","","القطر الخارجي","mm","15.9","15.9","15.9","","15.9","15.9"]
["","Level difference","IU - IU","Max.","م","0.5","0.5","0.5","","0.5","0.5"]
["","","IU - OU","Max.","م","30.0","30.0","30.0","","30.0","30.0"]
["","Additional refrigerant charge","","","kg/m","انظر دليل التركيب 4P302555-1","انظر دليل التركيب 4P302555-1","انظر دليل التركيب 4P302555-1","","انظر دليل التركيب 4P302555-1","انظر دليل التركيب 4P302555-1"]
["Sound power level","التبريد","","","dBA","64","64","66","","67","67"]
["Compressor","Type","","","","Hermetically sealed swing compressor","Hermetically sealed swing compressor","Hermetically sealed swing compressor","","Hermetically sealed swing compressor","Hermetically sealed swing compressor"]
["Dimensions","Unit","","العرض","mm","940","940","940","","940","940"]
["","","","العمق","mm","320","320","320","","320","320"]
["","","","الارتفاع","mm","990","990","1,430","","1,430","1,430"]
["الوزن","الوحدة","","","kg","78","80","101","","102","101"]
["Power supply","الطور","","","","1~","3N~","3N~","","1~","3N~"]
["","Frequency","","","Hz","50","50","50","","50","50"]
["","Voltage","","","V","220-240","380-415","380-415","","220-240","380-415"]
["Notes","","","","","(1) - PED: التجميع = الفئة l : مستثنى من مجال PED بسبب المقالة 1، الفقرة 3.6 من ‎97/23/EC","(1) - PED: التجميع = الفئة l : مستثنى من مجال PED بسبب المقالة 1، الفقرة 3.6 من ‎97/23/EC","(1) - PED: التجميع = الفئة l : مستثنى من مجال PED بسبب المقالة 1، الفقرة 3.6 من ‎97/23/EC","","(1) - PED: التجميع = الفئة l : مستثنى من مجال PED بسبب المقالة 1، الفقرة 3.6 من ‎97/23/EC","(1) - PED: التجميع = الفئة l : مستثنى من مجال PED بسبب المقالة 1، الفقرة 3.6 من ‎97/23/EC"]
["","","","","","(2) - Equipment complying with EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(2) - 3 مع إعادة الشحن","(2) - 3 مع إعادة الشحن","","(2) - Equipment complying with EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(2) - 3 مع إعادة الشحن"]
["","","","","","(3) - Short-circuit power","(3) - See separate drawing for electrical data","(3) - See separate drawing for electrical data","","(3) - Short-circuit power","(3) - See separate drawing for electrical data"]
["","","","","","(4) - See separate drawing for electrical data","(4) - يحتوي على غازات الاحتباس الحراري المفلورة","(4) - يحتوي على غازات الاحتباس الحراري المفلورة","","(4) - See separate drawing for electrical data","(4) - يحتوي على غازات الاحتباس الحراري المفلورة"]
["","","","","","(5) - 3 مع إعادة الشحن","","","","(5) - 3 مع إعادة الشحن"]
["","","","","","(6) - يحتوي على غازات الاحتباس الحراري المفلورة","","","","(6) - يحتوي على غازات الاحتباس الحراري المفلورة"]
["مستوى طاقة الصوت","التبريد","","","dBA","","","","66"]
["الأبعاد","الوحدة","","الارتفاع","mm","","","","1430"]
["","","","العرض","mm","","","","940"]
["","","","العمق","mm","","","","320"]
["الوزن","الوحدة","","","kg","","","","102"]
["Operation range","Cooling","Ambient","Min.","درجة بمقياس الحوجلة الجافة","","","","-15.0"]
["","","","Max.","درجة بمقياس الحوجلة الجافة","","","","50.0"]
["","Heating","Ambient","Min.","°مئوية مقياس الحوجلة الرطبة","","","","-20.0"]
["","","","Max.","°مئوية مقياس الحوجلة الرطبة","","","","15.5"]
["Sound pressure level","Cooling","","Nom.","dBA","","","","50"]
["","Heating","","Nom.","dBA","","","","52"]
["","Night quiet mode","","Level 1","dBA","","","","45"]
["سائل تبريد","السعة","","","kg","","","","4.0"]
["","السعة","","","tCO2Eq","","","","8.4"]
["","GWP","","","","","","","2087.5"]
["وصلات الأنابيب","طول الأنابيب","الحد الأعلى","الوحدة الخارجية - الوحدة الداخلية","م","","","","75"]
["Piping connections","Level difference","IU - OU","Max.","م","","","","30.0"]
["","","IU - IU","Max.","م","","","","0.5"]
["Standard Accessories","Tie-wraps","","","","","","","2"]
["Power supply","Frequency","","","Hz","","","","50"]
["Notes","","","","","","","","(5) - 3 مع إعادة الشحن"]