## Sheet1
SERIES |  | SKY AIR |  |  | SKY AIR |  | SKY AIR |  | SKY AIR |  |  | SKY AIR |  |  | SKY AIR
EDP MODE |  | YES |  |  | YES |  | YES |  | YES |  |  | YES |  |  | YES
APPLICATION |  | IT SERVICES, LABORATORIES, RETAILS |  |  | IT SERVICES, LABORATORIES, RETAILS |  | IT SERVICES, LABORATORIES, RETAILS |  | IT SERVICES, LABORATORIES, RETAILS |  |  | IT SERVICES, LABORATORIES, RETAILS |  |  | IT SERVICES, LABORATORIES, RETAILS
OUTDOOR + INDOOR UNIT |  | Mini SkyAir Alpha series |  |  | Large SkyAir |  | Large SkyAir |  | Alpha Series |  |  | Alpha Series |  |  | Alpha Series
OPERATION RANGE |  | -20 ÷ 50 °C |  |  | -20 ÷ 46 °C |  | -20 ÷ 46 °C |  | -20 ÷ 50 °C |  |  | -20 ÷ 50 °C |  |  | -20 ÷ 50 °C
MODEL | CAPACITY kW | 35+50 |  | 3.5 kW | 200 + 2x100 | 19 | 200+200 | 19 | 71+100 | 6.8 kW |  | 71+100 | 6.8 kW |  | 71+100 | 6.8 kW
|  | 50+60 |  | 5.0 kW | 200 + 3x71 | 19 | 250+250 | 22 | 100+140 | 9.5 kW |  | 100+2x71 | 9.5 kW |  | 100+2x71 | 9.5 kW
|  | 60+71 |  | 6.0 kW | 200 + 3x60 | 19 |  |  | 125+140 | 12.1 kW |  | 125+2x71 | 12.1 kW |  | 125+2x71 | 12.1kW
[5 empty] | 200 + 4x50 | 19 |  |  | 140+140 | 13.4 kW |  | 140+2x71 | 13.4 kW |  | 140+2x71 | 13.4 kW
[5 empty] | 250 + 2x125 | 22 |  |  | 100+2x71 | 9.5 kW
[5 empty] | 250 + 4x60 | 22 |  |  | 125+2x71 | 12.1 kW
[9 empty] | 140+2x71 | 13.4 kW
| SEER | 35+50 |  | 6.65 | 200 + 2x100 | 6,32 | 200+200 | 6.25 | 71+100 | 6.69 |  | 71+100 | 6.43 |  | 71+100 | 6.89
|  | 50+60 |  | 7.02 | 200 + 3x71 | 6.32 | 250+250 | 5.37 | 100+140 | 9.44 |  | 100+2x71 | 9.45 |  | 100+2x71 | 8.82
|  | 60+71 |  | 6.81 | 200 + 3x60 | 6.32 |  |  | 125+140 | n/a |  | 125+2x71 | n/a |  | 125+2x71 | n/a
[5 empty] | 200 + 4x50 | 7.14 |  |  | 140+140 | 6.42 |  | 140+2x71 | n/a |  | 140+2x71 | n/a
[5 empty] | 250 + 2x125 | 6.65 |  |  | 100+2x71 | 9.44
[5 empty] | 250 + 4x60 | 6.95 |  |  | 125+2x71 | n/a
[9 empty] | 140+2x71 | n/a
REFRIGERANT TYPE |  | R-32 |  |  | R-32 |  | R32 |  | R-32 |  |  | R-32 |  |  | R-32
PIPING LENGTH | L (OU-IU) | 50 m |  |  | 100 m |  | 100 m |  | 55 m (OU= 71) 82 m (OU=100/125/140) |  |  | 55 m (OU= 71) 82 m (OU=100) |  |  | 56 m (OU= 71) 82 m (OU=100/125)
| ΔH max, (OU-IU) | 30 m |  |  | 30 m |  | 30 m |  | 30 m |  |  | 30 m |  |  | 30 m
CONTROL OPTIONS
|  |  | Control system for infrastructure cooling |  |  | Unit |  | Integrating | [5 empty] | Advanced
[6 empty] | BRC1H51 (9) W/S/K |  | RTD-10 |  |  | DTA113851 |  |  | DCM601A51
[6 empty] | BRC1E53 A/B/C |  | (Server room) |  |  | (DS net) |  |  | (iTM)
[6 empty] | (1-1 group) |  | 1-1-1 (1 gateway for group, up to 8 gateways linked |  |  | 1-4 (1 adapter to 4 units) |  |  | 1-64 ( 1 iTM for 64 indoor units group)
|  |  | Automatic control of A/C |  |  | x |  | x |  |  | x |  |  | x
|  |  | Duty Rotation |  |  | x |  | x |  |  | x |  |  | x
|  |  | Back up |  |  | x |  | x |  |  | x |  |  | x
|  |  | Local control limitations |  |  | x |  | x | [5 empty] | x
|  |  | Temperature back up system |  |  |  |  | x | [5 empty] | x
|  |  | Error = alarm displayed |  |  | x |  | x | [5 empty] | x
|  |  | Error = activation of alarm |  |  | Via KRP4A |  | x | [5 empty] | Via WAGO I/O
|  |  | Easy setting/copy of setting and status read - out |  |  | x |  | x | [5 empty] | x
BACK-UP SYSTEM / DUTY ROTATION |  | To apply duty rotation and back up TWO sets of the same systems must be installed. The system will be connected by the controller. Duty rotation interval is changeable
SYSTEM COMBINATION
LAYOUT BEST PRACTICES |  | FHA-A ceiling suspended units |  |  | FCAG-B - cassette unit |  | FDA-A - concealed ceiling units |  | FHA-A ceiling suspended units |  |  | FAA-A - wall mounted units |  |  | FUA-A - casette unit
EU AVAILABILITY |  | available |  |  | available |  | available |  | available |  |  | available |  |  | available
RZAG
FHA-A
RZAG
FAA – A
RZAG
FUA-A
RZA-D
FCAG-B
FDA-A
RZA-D
RZAG-A
FHA - A
35
50
(P)aired system combination technical cooling
3.5 kW
50
5.0 kW
60
60
6.0 kW
71
Triple solution (3)
200
4x50
Double-twin (4)
4x60
250
Twin solution (2)
200
2x100
250
2x125
200
3x60
250
3x71
Refnet joint
Just one climate zone control
71
100
(P)aired system combination technical cooling
6.8 kW
(P)aired system combination technical cooling
100
125
140
140
9.5 kW
12.1 kW
13.5 kW
Refnet joint
Just one climate zone control
100
125
9.5 kW
12.1 kW
13.5 kW
140
2x71
Twin solution (2)
100
125
9.5 kW
12.1 kW
13.5 kW
140
2x71
Twin solution (2)
Refnet joint
Just one climate zone control
71
100
(P)aired system combination technical cooling
6.8 kW
71
100
(P)aired system combination technical cooling
6.8 kW
100
125
9.5 kW
12.1 kW
13.5 kW
140
2x71
Twin solution (2)
Refnet joint
Just one climate zone control
200
200
(P)aired system combination technical cooling
250
250
Asymetric solution benefits:
1. Less risk of defrost
2. Higher efficiecny - less costs during 24h /7 operation
3. Better humidity control