{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":70,"n_cols":21,"rows_kept":70,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWYT-B-SR"]
[]
[]
[]
[]
["","","","","","EWYT085B-SRA1","EWYT105B-SRA1","EWYT135B-SRA1","EWYT175B-SRA1","EWYT205B-SRA2","EWYT215B-SRA1","EWYT235B-SRA2","EWYT255B-SRA2","EWYT300B-SRA2","EWYT340B-SRA2","EWYT390B-SRA2","EWYT430B-SRA2","EWYT490B-SRA2","EWYT540B-SRA2","EWYT590B-SRA2","EWYT630B-SRA2"]
["Sound pressure level","Cooling","","Nom.","dBA","60","64","65","67","66","68","67","67","68","68","69","69.3","69.4","69.5","70","70.1"]
["Compressor","Type","","","","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor","Scroll compressor"]
["","Starting method","","","","Direct on line","Direct on line","Direct on line","Direct on line","Direct on line","Direct on line","Direct on line","","Direct on line","Direct on line","Direct on line","Direct on line","Direct on line","Direct on line","Direct on line","Direct on line"]
["","Quantity","","","","2","2","2","2","4","2","4","4","4","4","4","4","5","6","6","6"]
["Weight","Operation weight","","","kg","992","1,102","1,202","1,357","1,541","1,541","1,841","1,869","2,274","2,430","3,360","3,370","3,367","3,557","4,462","4,468"]
["","Unit","","","kg","985","1,095","1,195","1,350","1,530","1,530","1,830","1,855","2,260","2,410","3,340","3,350","3,340","3,530","4,427","4,427"]
["Air heat exchanger","Type","","","","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type","High efficiency fin and tube type"]
["EER","","","","","2.56","2.58","2.61","2.53","2.54","2.55","2.59","2.55","2.59","2.64","2.61","2.5","2.46","2.41","2.5","2.51"]
["Refrigerant","Type","","","","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32"]
["","Circuits","","Quantity","","","","","","","","","2"]
["","Charge","","","kg","13.3","14.7","19.3","24.5","29","34","36.2","43","40.3","47.2","50.4","79","58.5","68.8","77.6","82"]
["Cooling capacity","Nom.","","","kW","74","96","119","150","186","189","209","226","265","311","344","368","424","470","519","557"]
["Water heat exchanger","Water volume","","","l","","","","","","","","14"]
["","Type","","","","","","","","","","","Plate heat exchanger"]
["Power input","Cooling","","Nom.","kW","","","","","","","","88.8"]
["","Heating","","Nom.","kW","","","","","","","","86.29"]
["Sound power level","Cooling","","Nom.","dBA","78","82","84","85","84","87","86","86","87","88","89","89.3","89.4","89.5","90.4","90.5"]
["COP","","","","","","","","","","","","2.912"]
["Dimensions","Unit","","Width","mm","1,195","1,195","1,195","1,195","1,195","1,195","1,195","1,195","2,282","2,282","2,282","2,282","2,282","2,282","2,282","2,282"]
["","","","Depth","mm","2,225","2,825","3,425","3,425","4,350","4,025","4,950","4,950","3,225","3,225","4,125","4,125","4,125","4,125","5,025","5,025"]
["","","","Height","mm","1,800","1,800","1,800","1,800","1,800","1,800","1,800","1,800","2,514","2,514","2,514","2,514","2,514","2,514","2,514","2,514"]
["Capacity control","Minimum capacity","","","%","50","38","50","38","19","50","17","25","22","19","17","25","22","19","18","17"]
["","Method","","","","Step","Step","Step","Step","Step","Step","Step","Step","Step","Step","Step","Step","Step","Step","Step","Step"]
["Fan","Air flow rate","","Nom.","l/s","","","","","","","","18,078"]
["","Speed","","","rpm","","","","","","","","1,200"]
["Heating capacity","Nom.","","","kW","","","","","","","","251.28"]
["Compressor","Starting method","","","","","","","","","","","Direct on line"]
["Power supply","Phase","","","","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~","3~"]
["","Voltage range","","Max.","%","10","10","10","10","10","10","10","","10","10","10","10","10","10","10","10"]
["","","","Min.","%","-10","-10","-10","-10","-10","-10","-10","","-10","-10","-10","-10","-10","-10","-10","-10"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400","400"]
["Unit","Max unit current for wires sizing","","","A","75.0","94.0","111.0","144.0","183.0","179.0","201.0","","255.0","293.0","334.0","367.0","417.0","468.0","509.0","542.0"]
["","Starting current","","Max","A","211.0","327.0","343.0","464.0","408.0","495.0","425.0","","564.0","598.0","636.0","666.0","712.0","757.0","795.0","825.0"]
["","Running current","Cooling","Nom.","A","55.0","67.0","77.0","101.0","128.0","126.0","136.0","","173.0","196.0","224.0","251.0","292.0","330.0","353.0","373.0"]
["","","","Max","A","68.0","85.0","101.0","131.0","166.0","163.0","183.0","","232.0","266.0","304.0","334.0","379.0","425.0","463.0","493.0"]
["Notes","","","","","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: 12,0/7,0°C; ambient 35,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: 12,0/7,0°C; ambient 35,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: 12,0/7,0°C; ambient 35,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: 12,0/7,0°C; ambient 35,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: 12,0/7,0°C; ambient 35,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: 12,0/7,0°C; ambient 35,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: 12,0/7,0°C; ambient 35,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: 12,0/7,0°C; ambient 35,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: 12,0/7,0°C; ambient 35,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: 12,0/7,0°C; ambient 35,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: 12,0/7,0°C; ambient 35,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: 12,0/7,0°C; ambient 35,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: 12,0/7,0°C; ambient 35,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: 12,0/7,0°C; ambient 35,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: 12,0/7,0°C; ambient 35,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(1) - All the performances (Cooling capacity, unit power input in cooling and EER) are based on the following conditions: 12,0/7,0°C; ambient 35,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018"]
["","","","","","(2) - All the performances (Heating capacity, unit power input in heating and COP) are based on the following conditions: 40,0/45,0°C; ambient 7,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(2) - All the performances (Heating capacity, unit power input in heating and COP) are based on the following conditions: 40,0/45,0°C; ambient 7,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(2) - All the performances (Heating capacity, unit power input in heating and COP) are based on the following conditions: 40,0/45,0°C; ambient 7,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(2) - All the performances (Heating capacity, unit power input in heating and COP) are based on the following conditions: 40,0/45,0°C; ambient 7,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(2) - All the performances (Heating capacity, unit power input in heating and COP) are based on the following conditions: 40,0/45,0°C; ambient 7,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(2) - All the performances (Heating capacity, unit power input in heating and COP) are based on the following conditions: 40,0/45,0°C; ambient 7,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(2) - All the performances (Heating capacity, unit power input in heating and COP) are based on the following conditions: 40,0/45,0°C; ambient 7,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(2) - All the performances (Heating capacity, unit power input in heating and COP) are based on the following conditions: 40,0/45,0°C; ambient 7,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(2) - All the performances (Heating capacity, unit power input in heating and COP) are based on the following conditions: 40,0/45,0°C; ambient 7,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(2) - All the performances (Heating capacity, unit power input in heating and COP) are based on the following conditions: 40,0/45,0°C; ambient 7,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(2) - All the performances (Heating capacity, unit power input in heating and COP) are based on the following conditions: 40,0/45,0°C; ambient 7,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(2) - All the performances (Heating capacity, unit power input in heating and COP) are based on the following conditions: 40,0/45,0°C; ambient 7,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(2) - All the performances (Heating capacity, unit power input in heating and COP) are based on the following conditions: 40,0/45,0°C; ambient 7,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(2) - All the performances (Heating capacity, unit power input in heating and COP) are based on the following conditions: 40,0/45,0°C; ambient 7,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(2) - All the performances (Heating capacity, unit power input in heating and COP) are based on the following conditions: 40,0/45,0°C; ambient 7,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018","(2) - All the performances (Heating capacity, unit power input in heating and COP) are based on the following conditions: 40,0/45,0°C; ambient 7,0°C, unit at full load operation; operating fluid: Water; fouling factor = 0. EN14511:2018"]
["","","","","","(3) - SCOP is based on the following conditions: Tbivalent -5 °C, Tdesign -10 °C, Average ambient conditions, Ref. EN14825. In accordance with standard EN14825, comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) N","(3) - SCOP is based on the following conditions: Tbivalent -5 °C, Tdesign -10 °C, Average ambient conditions, Ref. EN14825. In accordance with standard EN14825, comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) N","(3) - SCOP is based on the following conditions: Tbivalent -5 °C, Tdesign -10 °C, Average ambient conditions, Ref. EN14825. In accordance with standard EN14825, comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) N","(3) - SCOP is based on the following conditions: Tbivalent -5 °C, Tdesign -10 °C, Average ambient conditions, Ref. EN14825. In accordance with standard EN14825, comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) N","(3) - SCOP is based on the following conditions: Tbivalent -5 °C, Tdesign -10 °C, Average ambient conditions, Ref. EN14825. In accordance with standard EN14825, comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) N","(3) - SCOP is based on the following conditions: Tbivalent -5 °C, Tdesign -10 °C, Average ambient conditions, Ref. EN14825. In accordance with standard EN14825, comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) N","(3) - SCOP is based on the following conditions: Tbivalent -5 °C, Tdesign -10 °C, Average ambient conditions, Ref. EN14825. In accordance with standard EN14825, comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) N","(3) - SCOP is based on the following conditions: Tbivalent -5 °C, Tdesign -10 °C, Average ambient conditions, Ref. EN14825. In accordance with standard EN14825, comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) No 2016/2281;","(3) - SCOP is based on the following conditions: Tbivalent -5 °C, Tdesign -10 °C, Average ambient conditions, Ref. EN14825. In accordance with standard EN14825, comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) N","(3) - SCOP is based on the following conditions: Tbivalent -5 °C, Tdesign -10 °C, Average ambient conditions, Ref. EN14825. In accordance with standard EN14825, comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) N","(3) - SCOP is based on the following conditions: Tbivalent -5 °C, Tdesign -10 °C, Average ambient conditions, Ref. EN14825. In accordance with standard EN14825, comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) N","(3) - SCOP is based on the following conditions: Tbivalent -5 °C, Tdesign -10 °C, Average ambient conditions, Ref. EN14825. In accordance with standard EN14825, comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) N","(3) - SCOP is based on the following conditions: Tbivalent -5 °C, Tdesign -10 °C, Average ambient conditions, Ref. EN14825. In accordance with standard EN14825, comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) N","(3) - SCOP is based on the following conditions: Tbivalent -5 °C, Tdesign -10 °C, Average ambient conditions, Ref. EN14825. In accordance with standard EN14825, comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) N","(3) - SCOP is based on the following conditions: Tbivalent -5 °C, Tdesign -10 °C, Average ambient conditions, Ref. EN14825. In accordance with standard EN14825, comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) N","(3) - SCOP is based on the following conditions: Tbivalent -5 °C, Tdesign -10 °C, Average ambient conditions, Ref. EN14825. In accordance with standard EN14825, comfort low temperature, average climate, SEER and µs values applicable Ecodesign regulation: (EU) N"]
["","","","","","(4) - PHE: Plate Heat Exchanger; S&T: Single Pass Shell & Tube; MCH: Microchannel; DPT: Direct Propeller Type; DOL: Direct On Line - VFD: Inverter","(4) - PHE: Plate Heat Exchanger; S&T: Single Pass Shell & Tube; MCH: Microchannel; DPT: Direct Propeller Type; DOL: Direct On Line - VFD: Inverter","(4) - PHE: Plate Heat Exchanger; S&T: Single Pass Shell & Tube; MCH: Microchannel; DPT: Direct Propeller Type; DOL: Direct On Line - VFD: Inverter","(4) - PHE: Plate Heat Exchanger; S&T: Single Pass Shell & Tube; MCH: Microchannel; DPT: Direct Propeller Type; DOL: Direct On Line - VFD: Inverter","(4) - PHE: Plate Heat Exchanger; S&T: Single Pass Shell & Tube; MCH: Microchannel; DPT: Direct Propeller Type; DOL: Direct On Line - VFD: Inverter","(4) - PHE: Plate Heat Exchanger; S&T: Single Pass Shell & Tube; MCH: Microchannel; DPT: Direct Propeller Type; DOL: Direct On Line - VFD: Inverter","(4) - PHE: Plate Heat Exchanger; S&T: Single Pass Shell & Tube; MCH: Microchannel; DPT: Direct Propeller Type; DOL: Direct On Line - VFD: Inverter","(4) - PHE: Plate Heat Exchanger; S&T: Single Pass Shell & Tube; MCH: Microchannel; DPT: Direct Propeller Type; DOL: Direct On Line - VFD: Inverter","(4) - PHE: Plate Heat Exchanger; S&T: Single Pass Shell & Tube; MCH: Microchannel; DPT: Direct Propeller Type; DOL: Direct On Line - VFD: Inverter","(4) - PHE: Plate Heat Exchanger; S&T: Single Pass Shell & Tube; MCH: Microchannel; DPT: Direct Propeller Type; DOL: Direct On Line - VFD: Inverter","(4) - PHE: Plate Heat Exchanger; S&T: Single Pass Shell & Tube; MCH: Microchannel; DPT: Direct Propeller Type; DOL: Direct On Line - VFD: Inverter","(4) - PHE: Plate Heat Exchanger; S&T: Single Pass Shell & Tube; MCH: Microchannel; DPT: Direct Propeller Type; DOL: Direct On Line - VFD: Inverter","(4) - PHE: Plate Heat Exchanger; S&T: Single Pass Shell & Tube; MCH: Microchannel; DPT: Direct Propeller Type; DOL: Direct On Line - VFD: Inverter","(4) - PHE: Plate Heat Exchanger; S&T: Single Pass Shell & Tube; MCH: Microchannel; DPT: Direct Propeller Type; DOL: Direct On Line - VFD: Inverter","(4) - PHE: Plate Heat Exchanger; S&T: Single Pass Shell & Tube; MCH: Microchannel; DPT: Direct Propeller Type; DOL: Direct On Line - VFD: Inverter","(4) - PHE: Plate Heat Exchanger; S&T: Single Pass Shell & Tube; MCH: Microchannel; DPT: Direct Propeller Type; DOL: Direct On Line - VFD: Inverter"]
["","","","","","(5) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(5) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(5) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(5) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(5) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(5) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(5) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(5) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for info only, not considered bounding","(5) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(5) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(5) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(5) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(5) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(5) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(5) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i","(5) - Sound power (evap. 12/7°C, ambient 35°C full load operation) in accordance with ISO9614 and Eurovent 8/1 for Eurovent certified units. Certification refers only to the overall sound power, sound pressure is calculated from sound power level and used for i"]
["","","","","","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition","(6) - The minimum capacity indicated is referred to unit operating at standard Eurovent condition"]
["","","","","","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request.","(7) - Dimensions and weights are for indication only and are not considered binding. Before designing the installation, consult the official drawings available from the factory on request."]
["","","","","","(8) - The data are referred to the unit without additional options.","(8) - The data are referred to the unit without additional options.","(8) - The data are referred to the unit without additional options.","(8) - The data are referred to the unit without additional options.","(8) - The data are referred to the unit without additional options.","(8) - The data are referred to the unit without additional options.","(8) - The data are referred to the unit without additional options.","(8) - The data are referred to the unit without additional options.","(8) - The data are referred to the unit without additional options.","(8) - The data are referred to the unit without additional options.","(8) - The data are referred to the unit without additional options.","(8) - The data are referred to the unit without additional options.","(8) - The data are referred to the unit without additional options.","(8) - The data are referred to the unit without additional options.","(8) - The data are referred to the unit without additional options.","(8) - The data are referred to the unit without additional options."]
["","","","","","(9) - The values of the Pressure Drops refers to the pressure drops in the Water heat exchanger only.","(9) - The values of the Pressure Drops refers to the pressure drops in the Water heat exchanger only.","(9) - The values of the Pressure Drops refers to the pressure drops in the Water heat exchanger only.","(9) - The values of the Pressure Drops refers to the pressure drops in the Water heat exchanger only.","(9) - The values of the Pressure Drops refers to the pressure drops in the Water heat exchanger only.","(9) - The values of the Pressure Drops refers to the pressure drops in the Water heat exchanger only.","(9) - The values of the Pressure Drops refers to the pressure drops in the Water heat exchanger only.","(9) - The values of the Pressure Drops refers to the pressure drops in the Water heat exchanger only.","(9) - The values of the Pressure Drops refers to the pressure drops in the Water heat exchanger only.","(9) - The values of the Pressure Drops refers to the pressure drops in the Water heat exchanger only.","(9) - The values of the Pressure Drops refers to the pressure drops in the Water heat exchanger only.","(9) - The values of the Pressure Drops refers to the pressure drops in the Water heat exchanger only.","(9) - The values of the Pressure Drops refers to the pressure drops in the Water heat exchanger only.","(9) - The values of the Pressure Drops refers to the pressure drops in the Water heat exchanger only.","(9) - The values of the Pressure Drops refers to the pressure drops in the Water heat exchanger only.","(9) - The values of the Pressure Drops refers to the pressure drops in the Water heat exchanger only."]
["","","","","","(10) - Fluid: Water","(10) - Fluid: Water","(10) - Fluid: Water","(10) - Fluid: Water","(10) - Fluid: Water","(10) - Fluid: Water","(10) - Fluid: Water","(10) - Fluid: Water","(10) - Fluid: Water","(10) - Fluid: Water","(10) - Fluid: Water","(10) - Fluid: Water","(10) - Fluid: Water","(10) - Fluid: Water","(10) - Fluid: Water","(10) - Fluid: Water"]
["","","","","","(11) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(11) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(11) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(11) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(11) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(11) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(11) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(11) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(11) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(11) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(11) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(11) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(11) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(11) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(11) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%.","(11) - Allowed voltage tolerance ± 10%. Voltage unbalance between phases must be within ± 3%."]
["","","","","","(12) - Maximum starting current: In case of inverter driven units, no inrush current at start up is experienced.","(12) - Maximum starting current: In case of inverter driven units, no inrush current at start up is experienced.","(12) - Maximum starting current: In case of inverter driven units, no inrush current at start up is experienced.","(12) - Maximum starting current: In case of inverter driven units, no inrush current at start up is experienced.","(12) - Maximum starting current: In case of inverter driven units, no inrush current at start up is experienced.","(12) - Maximum starting current: In case of inverter driven units, no inrush current at start up is experienced.","(12) - Maximum starting current: In case of inverter driven units, no inrush current at start up is experienced.","(12) - Maximum starting current: In case of inverter driven units, no inrush current at start up is experienced.","(12) - Maximum starting current: In case of inverter driven units, no inrush current at start up is experienced.","(12) - Maximum starting current: In case of inverter driven units, no inrush current at start up is experienced.","(12) - Maximum starting current: In case of inverter driven units, no inrush current at start up is experienced.","(12) - Maximum starting current: In case of inverter driven units, no inrush current at start up is experienced.","(12) - Maximum starting current: In case of inverter driven units, no inrush current at start up is experienced.","(12) - Maximum starting current: In case of inverter driven units, no inrush current at start up is experienced.","(12) - Maximum starting current: In case of inverter driven units, no inrush current at start up is experienced.","(12) - Maximum starting current: In case of inverter driven units, no inrush current at start up is experienced."]
["","","","","","(13) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","(13) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","(13) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","(13) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","(13) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","(13) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","(13) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","(13) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","(13) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","(13) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","(13) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","(13) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","(13) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","(13) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","(13) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current","(13) - Nominal current in cooling mode is referred to the following conditions: Water Side Heat Exchanger 12/7°C; ambient 35°C; compressors + fans current"]
["","","","","","(14) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","(14) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","(14) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","(14) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","(14) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","(14) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","(14) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","(14) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","(14) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","(14) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","(14) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","(14) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","(14) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","(14) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","(14) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current.","(14) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current."]
["","","","","","(15) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(15) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(15) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(15) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(15) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(15) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(15) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(15) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(15) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(15) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(15) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(15) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(15) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(15) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(15) - Maximum unit current for wires sizing is based on minimum allowed voltage.","(15) - Maximum unit current for wires sizing is based on minimum allowed voltage."]
["","","","","","(16) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(16) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(16) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(16) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(16) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(16) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(16) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(16) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(16) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(16) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(16) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(16) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(16) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(16) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(16) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1","(16) - Maximum current for wires sizing: (compressors full load ampere + fans current) x 1.1"]
["","","","","","(17) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(17) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(17) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(17) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(17) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(17) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(17) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(17) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(17) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(17) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(17) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(17) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(17) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(17) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(17) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book","(17) - For the electrical data of the hydronic kit refer to \"Options technical data\" part in the data book"]
["","","","","","(18) - All data are subject to change without notice. Please refer to the unit nameplate data.","(18) - All data are subject to change without notice. Please refer to the unit nameplate data.","(18) - All data are subject to change without notice. Please refer to the unit nameplate data.","(18) - All data are subject to change without notice. Please refer to the unit nameplate data.","(18) - All data are subject to change without notice. Please refer to the unit nameplate data.","(18) - All data are subject to change without notice. Please refer to the unit nameplate data.","(18) - All data are subject to change without notice. Please refer to the unit nameplate data.","(18) - All data are subject to change without notice. Please refer to the unit nameplate data.","(18) - All data are subject to change without notice. Please refer to the unit nameplate data.","(18) - All data are subject to change without notice. Please refer to the unit nameplate data.","(18) - All data are subject to change without notice. Please refer to the unit nameplate data.","(18) - All data are subject to change without notice. Please refer to the unit nameplate data.","(18) - All data are subject to change without notice. Please refer to the unit nameplate data.","(18) - All data are subject to change without notice. Please refer to the unit nameplate data.","(18) - All data are subject to change without notice. Please refer to the unit nameplate data.","(18) - All data are subject to change without notice. Please refer to the unit nameplate data."]
["Refrigerant","Circuits","","Quantity","","1","1","1","1","2","1","2","","2","2","2","2","2","2","2","2"]
["Fan motor","Drive","","","","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven"]
["IPLV","","","","","4.36","4.24","4.3","4.38","4.29","4.29","4.28","","4.29","4.69","4.58","4.61","4.78","4.89","4.82","4.91"]
["Piping connections","Evaporator water inlet/outlet (OD)","","","","88.9","88.9","88.9","88.9","88.9","88.9","88.9","","88.9","88.9","88.9","88.9","88.9","88.9","88.9","88.9"]
["SEER","","","","","3.82","3.93","3.87","3.96","3.92","3.82","3.83","","4.18","4.37","4.21","4.19","4.49","4.49","4.46","4.52"]
["Power input","Cooling","","Nom.","kW","28.7","37.4","45.5","59.5","73.2","74.3","80.7","","102","117","131","147","172","195","207","221"]
["Casing","Material","","","","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet"]
["","Colour","","","","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white"]
["Fan","Type","","","","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller","Direct propeller"]
["","Quantity","","","","4","6","8","8","10","10","12","","5","6","8","8","8","8","10","10"]