{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":48,"n_cols":9,"rows_kept":48,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWC-BF"]
[]
[]
[]
[]
["","","","","","FWC06B5FV1B","FWC07B5FV1B","FWC08B5FV1B","FWC09B5FV1B"]
["Sound pressure level","Low","","","dBA","21.0","22.0","24.0","28.0"]
["","High","","","dBA","29.0","33.0","39.0","43.0"]
["Standard Accessories","Installation and operation manual","","","","1","1","1","1"]
["","Installation guide","","","","1","1","1","1"]
["","Drain hose","","","","1","1","1","1"]
["","Metal clamp for drain hose","","","","1","1","1","1"]
["","Washer for hanger bracket","","","","8","8","8","8"]
["","Screws","","","","4","4","4","4"]
["","O ring","","","","4","4","4","4"]
["","Insulation","","","","6","6","6","6"]
["Total sound power level","Low","","","dBA","33.0","36.0","36.0","40.0"]
["","High","","","dBA","43.0","47.0","53.0","57.0"]
["Water flow","Water pressure drop","Heating","High","kPa","18","22","30","38"]
["","","Cooling","High","kPa","15","18","23","30"]
["Piping connections","Drain","","OD","mm","VP25 (External dia.32, internal dia. 25)","VP25 (External dia.32, internal dia. 25)","VP25 (External dia.32, internal dia. 25)","VP25 (External dia.32, internal dia. 25)"]
["","Water","","Inlet","","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)"]
["","","","Outlet","","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)"]
["Power input","High","","","kW","0.046","0.055","0.077","0.107"]
["","Low","","","kW","0.035","0.038","0.040","0.046"]
["Allowed water temperature","Heating","","Max.","°C","70 (4)","70 (4)","70 (4)","70 (4)"]
["","","","Min.","°C","5 (4)","5 (4)","5 (4)","5 (4)"]
["","Cooling","","Min.","°C","5 (4)","5 (4)","5 (4)","5 (4)"]
["","","","Max.","°C","70 (4)","70 (4)","70 (4)","70 (4)"]
["Dimensions","Unit","","Width","mm","840","840","840","840"]
["","","","Depth","mm","840","840","840","840"]
["","","","Height","mm","288","288","288","288"]
["Weight","Unit","","","kg","29","29","29","29"]
["Fan","Air flow rate","","Low","m³/h","708","804","852","1,014"]
["","","","High","m³/h","1,032","1,200","1,476","1,746"]
["Cooling capacity (standard conditions)","Total capacity 4-pipe","","Low","kW","4.3 (1)","4.6 (1)","4.8 (1)","5.7 (1)"]
["","","","High","kW","5.9 (1)","6.3 (1)","7.2 (1)","8.3 (1)"]
["","Sensible capacity 4-pipe","","Low","kW","3.1 (1)","3.3 (1)","3.5 (1)","4.0 (1)"]
["","","","High","kW","4.2 (1)","4.6 (1)","5.4 (1)","6.4 (1)"]
["Heating capacity (standard conditions)","Capacity 4-pipe","","Low","kW","5.2 (3)","5.5 (3)","5.8 (3)","6.8 (3)"]
["","","","High","kW","6.9 (3)","7.8 (3)","9.2 (3)","10.4 (3)"]
["Power supply","Phase","","","","1~","1~","1~","1~"]
["","Frequency","","","Hz","50","50","50","50"]
["","Voltage","","","V","220-240","220-240","220-240","220-240"]
["Notes","","","","","(1) - Cooling: air 27°CDB, 19°CWB; entering water 7°C; leaving water 12°C","(1) - Cooling: air 27°CDB, 19°CWB; entering water 7°C; leaving water 12°C","(1) - Cooling: air 27°CDB, 19°CWB; entering water 7°C; leaving water 12°C","(1) - Cooling: air 27°CDB, 19°CWB; entering water 7°C; leaving water 12°C"]
["","","","","","(2) - Heating: 2 pipe: air 20°CDB, 15°CWB; entering water 45°C; leaving water 40°C","(2) - Heating: 2 pipe: air 20°CDB, 15°CWB; entering water 45°C; leaving water 40°C","(2) - Heating: 2 pipe: air 20°CDB, 15°CWB; entering water 45°C; leaving water 40°C","(2) - Heating: 2 pipe: air 20°CDB, 15°CWB; entering water 45°C; leaving water 40°C"]
["","","","","","(3) - Heating: 4 pipe: air 20°CDB, 15°CWB; entering water 65°C; leaving water 55°C","(3) - Heating: 4 pipe: air 20°CDB, 15°CWB; entering water 65°C; leaving water 55°C","(3) - Heating: 4 pipe: air 20°CDB, 15°CWB; entering water 65°C; leaving water 55°C","(3) - Heating: 4 pipe: air 20°CDB, 15°CWB; entering water 65°C; leaving water 55°C"]
["","","","","","(4) - Do not let water of less than 5°C or more than 50°/70°C enter the unit, this may damage the unit","(4) - Do not let water of less than 5°C or more than 50°/70°C enter the unit, this may damage the unit","(4) - Do not let water of less than 5°C or more than 50°/70°C enter the unit, this may damage the unit","(4) - Do not let water of less than 5°C or more than 50°/70°C enter the unit, this may damage the unit"]