{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":49,"n_cols":9,"rows_kept":49,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWF-BF"]
[]
[]
[]
[]
["","","","","","FWF02B5FV1B","FWF03B5FV1B","FWF04B5FV1B","FWF05B5FV1B"]
["Sound pressure level","Low","","","dBA","26.0","27.0","27.0","32.0"]
["","High","","","dBA","31.0","33.0","42.0","47.0"]
["Standard Accessories","Installation and operation manual","","","","1","1","1","1"]
["","Drain hose","","","","1","1","1","1"]
["","Clamp for drain hose","","","","1","1","1","1"]
["","Washer for hanger bracket","","","","8","8","8","8"]
["","Screws","","","","4","4","4","4"]
["","Installation guide","","","","1","1","1","1"]
["","O ring","","","","4","4","4","4"]
["","Insulation","","","","8","8","8","8"]
["Total sound power level","Low","","","dBA","36.0","38.0","41.0","44.0"]
["","High","","","dBA","44.0","46.0","52.0","57.0"]
["Water flow","Water pressure drop","Heating","High","kPa","9","5","9","13"]
["","","Cooling","High","kPa","6","16","26","38"]
["Piping connections","Drain","","OD","mm","VP20 (External dia.26, Internal dia. 20)","VP20 (External dia.26, Internal dia. 20)","VP20 (External dia.26, Internal dia. 20)","VP20 (External dia.26, Internal dia. 20)"]
["","Water","","Inlet","","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)"]
["","","","Outlet","","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)","3/4\" BSP (female thread)"]
["Power input","High","","","kW","0.074","0.074","0.094","0.121"]
["","Low","","","kW","0.060","0.055","0.055","0.066"]
["Allowed water temperature","Heating","","Max.","°C","70 (5)","70 (5)","70 (5)","70 (5)"]
["","","","Min.","°C","5 (5)","5 (5)","5 (5)","5 (5)"]
["","Cooling","","Min.","°C","5 (5)","5 (5)","5 (5)","5 (5)"]
["","","","Max.","°C","70 (5)","70 (5)","70 (5)","70 (5)"]
["Dimensions","Unit","","Width","mm","575","575","575","575"]
["","","","Depth","mm","575","575","575","575"]
["","","","Height","mm","285 (4)","285 (4)","285 (4)","285 (4)"]
["Weight","Unit","","","kg","20","20","20","20"]
["Fan","Air flow rate","","Low","m³/h","318","300","300","390"]
["","","","High","m³/h","468","438","618","822"]
["Cooling capacity (standard conditions)","Total capacity 4-pipe","","Low","kW","1.3 (1)","1.6 (1)","1.6 (1)","2.6 (1)"]
["","","","High","kW","1.8 (1)","2.9 (1)","3.8 (1)","4.6 (1)"]
["","Sensible capacity 4-pipe","","Low","kW","1.0 (1)","1.0 (1)","1.0 (1)","1.6 (1)"]
["","","","High","kW","1.5 (1)","1.8 (1)","2.5 (1)","3.2 (1)"]
["Heating capacity (standard conditions)","Capacity 4-pipe","","Low","kW","2.4 (3)","2.6 (3)","2.6 (3)","3.2 (3)"]
["","","","High","kW","3.3 (3)","3.6 (3)","4.7 (3)","5.7 (3)"]
["Power supply","Phase","","","","1~","1~","1~","1~"]
["","Frequency","","","Hz","50","50","50","50"]
["","Voltage","","","V","220-440","220-440","220-440","220-440"]
["Notes","","","","","(1) - Cooling: air 27°CDB, 19°CWB; entering water 7°C; leaving water 12°C","(1) - Cooling: air 27°CDB, 19°CWB; entering water 7°C; leaving water 12°C","(1) - Cooling: air 27°CDB, 19°CWB; entering water 7°C; leaving water 12°C","(1) - Cooling: air 27°CDB, 19°CWB; entering water 7°C; leaving water 12°C"]
["","","","","","(2) - Heating: 2 pipe: air 20°CDB, 15°CWB; entering water 45°C; leaving water 40°C","(2) - Heating: 2 pipe: air 20°CDB, 15°CWB; entering water 45°C; leaving water 40°C","(2) - Heating: 2 pipe: air 20°CDB, 15°CWB; entering water 45°C; leaving water 40°C","(2) - Heating: 2 pipe: air 20°CDB, 15°CWB; entering water 45°C; leaving water 40°C"]
["","","","","","(3) - Heating: 4 pipe: air 20°CDB, 15°CWB; entering water 65°C; leaving water 55°C","(3) - Heating: 4 pipe: air 20°CDB, 15°CWB; entering water 65°C; leaving water 55°C","(3) - Heating: 4 pipe: air 20°CDB, 15°CWB; entering water 65°C; leaving water 55°C","(3) - Heating: 4 pipe: air 20°CDB, 15°CWB; entering water 65°C; leaving water 55°C"]
["","","","","","(4) - Height includes switch box","(4) - Height includes switch box","(4) - Height includes switch box","(4) - Height includes switch box"]
["","","","","","(5) - Do not let water of less than 5°C or more than 50°/70°C enter the unit, this may damage the unit","(5) - Do not let water of less than 5°C or more than 50°/70°C enter the unit, this may damage the unit","(5) - Do not let water of less than 5°C or more than 50°/70°C enter the unit, this may damage the unit","(5) - Do not let water of less than 5°C or more than 50°/70°C enter the unit, this may damage the unit"]